	
	City of Texas City


Memo

To:
Rita Williams, Purchasing Dept.
From:
Ron Dysart, Storm Water Manager
Date:
4/27/2009
Re:
Ashland TR-1200
In 1998 the City installed a, REX Trash Rake to improve the debris removal that accumulates in the fore bay area of Pump Station “B”.  Debris removal is an ongoing condition that exists during every rain event at the station and must be removed immediately or the pumping operations will come to a halt, subsequent flooding will occur.
In approximately spring 2007, the City received a severe rain event that inundated the Pump Station to the point where debris was stacked against the bar screens to produce a 10-12 foot differential.  The pressure was so severe that the footer on the extreme east end of the structure broke numerous anchors which subsequently caused the entire structure to fail.  The Pump Station ceased pumping operation for a period of time and the City had to implement emergency repairs to the structure to allow for operations to continue.
The current rake configuration is inadequate for the increasing debris loads placed upon the bar screens.  The TR-1200 has the capability to lower cycle times of debris removal during rain events, which in turn will allow for continuous, uninterrupted pumping operations.
1
1
( Page 2

