[image: image1.png]SimplexGrinnell
BE SAFE.

A business unit of Tyco Fire & Security







  




             
SimplexGrinnell








                                                1200 E. Hackberry, Ste A







                                                McAllen, Texas 78501







                                                (956) 618-5284 Office







                                                (956) 686-9045 Fax












www.simplexgrinnell.com
March 24, 2008






*** This proposal is in accordance with TXMAS pricing
Attn: Daniel Flores




(TXMAS Contract #   TXMAS-5-84070)
Hidalgo County Buildings & Grounds
Re: Hidalgo County Courthouse – Un-install & Re-install / Re-wire 3 Panels to monitoring room
Dear Daniel,

Following is the quotation for the work that needs to be done at the Hidalgo County Courthouse.  Per the Captain, he has verbally given the okay to remove all three panels & keypad from the detention center and would like them to be re-wired and re-located to the monitoring room so that his guards do not have to leave their post every time the alarm goes off for fire alarm, access control or panic buttons.  Also, after we diagnosed the problems with the panels, we found that at least 1/3 of the existing panic buttons that go into the judges courts are not even working.  We also found that there are a series of “spiders’ nests” of cut, loose or miss-directed wires going to the panels.  This proposal also includes tracing these wires, or running new ones to replace the non-functioning panic buttons.  This also includes re-wiring all three systems that are causing continuous false alarms, on many occasions, several times a day to the new location.  This project should take at least two weeks to eliminate all false alarms via Fire, Panic or Access Control Systems.  Please don’t hesitate to call me if you have any questions pertaining to this proposal.

1
Replacement of bad existing Notifier AFP-200 Panel
2
Batteries for Notifier AFP-200 Panel

1
all wiring, 18/2, 16/2, 16/4 needed to re-run the 3 panels from the detention center to the monitoring center.

1
Labor for re-wiring 3 panels from detention center to monitoring center

1
Labor for un-installing & re-installing 3 panels (including new Notifier Panel)

1
Programming of all 3 panels once re-installed in the monitoring station

1
Panic Button for the Attorney’s Library

1
Mini-Module for Notifier AFP-200 Panel

1
includes any and all back boxes needed for scope of work

1
9600-0101
Installation Material









Grand total 

$17,415.50
· Excludes sales tax.  Excludes cutting, patching & painting.  Electrician / Customer to provide dedicated 110 for FACP/ Panels.  

Thank you for the opportunity to be of service.

Christopher MacDonald



_______________________

________
ESSR





                      Accepted by


   Date
Cell: 956-239-2241
chrmacdonald@tycoint.com
� EMBED MSPhotoEd.3  ���








_1243420959.bin

